Storm Water Pollution Prevention Plan (SWPPP)
Project Name 





Contract No. 





MOJAVE RIVER WATERSHED Water Quality Management Plan (WQMP)


MOJAVE RIVER WATERSHED
Water Quality Management Plan 

For:

Insert Project Name
where applicable, insert Grading Permit No., Building Permit No., Tract Number, Land development file no., CUP, SUP and/or APN (Specify Lot Numbers if site is a portion of a Tract)
Prepared for:

Insert Owner/Developer Name
Insert Address
Insert City, State, ZIP
Insert Telephone
Prepared by:

Insert Consulting/Engineering Firm Name
Insert Address
Insert City, State, ZIP
Insert Telephone
Submittal Date:  Insert Initial Submittal Date
Revision No. and  Date:  Insert No and Current Revision Date
Revision No. and  Date:  Insert No and Current Revision Date
Revision No. and  Date:  Insert No and Current Revision Date
Revision No. and  Date:  Insert No and Current Revision Date
Revision No. and  Date:  Insert No and Current Revision Date
Final Approval Date:_____________________
Project Owner’s Certification
This Mojave River Watershed Water Quality Management Plan (WQMP) has been prepared for Insert Owner/Developer Name by Insert Consulting/Engineering Firm Name. The WQMP is intended to comply with the requirements of the Insert Jurisdiction and the Phase II Small MS4 General Permit for the Mojave River Watershed. The undersigned, while it owns the subject property, is responsible for the implementation of the provisions of this plan and will ensure that this plan is amended as appropriate to reflect up-to-date conditions on the site consistent with the Phase II Small MS4 Permit and the intent of San Bernardino County (unincorporated areas of Phelan, Oak Hills, Spring Valley Lake and Victorville) and the incorporated cities of Hesperia and Victorville and the Town of Apple Valley. Once the undersigned transfers its interest in the property, its successors in interest and the city/county/town shall be notified of the transfer. The new owner will be informed of its responsibility under this WQMP. A copy of the approved WQMP shall be available on the subject site in perpetuity.

“I certify under a penalty of law that the provisions (implementation, operation, maintenance, and funding) of the WQMP have been accepted and that the plan will be transferred to future successors.”

	Project Data

	Permit/Application Number(s):
	     
	Grading Permit Number(s):
	     

	Tract/Parcel Map Number(s):
	     
	Building Permit Number(s):
	     

	CUP, SUP, and/or APN (Specify Lot Numbers if Portions of Tract):
	     

	Owner’s Signature

	Owner Name:      

	Title
	     

	Company
	     

	Address
	     

	Email
	     

	Telephone #
	     

	Signature
	
	Date
	     


Preparer’s Certification

	Project Data

	Permit/Application Number(s):
	     
	Grading Permit Number(s):
	     

	Tract/Parcel Map Number(s):
	     
	Building Permit Number(s):
	     

	CUP, SUP, and/or APN (Specify Lot Numbers if Portions of Tract):
	     


“The selection, sizing and design of stormwater treatment and other stormwater quality and quantity control measures in this plan were prepared under my oversight and meet the requirements of the California State Water Resources Control Board Order No. 2013-0001-DWQ. 
	Engineer:       
	PE Stamp Below

	Title
	     
	

	Company
	     
	

	Address
	     
	

	Email
	     
	

	Telephone #
	     
	

	Signature
	
	

	Date
	
	


Table of Contents

Section I
Introduction

Section 1
Discretionary Permits

1-1

Section 2 Project Description

2-1

2.1 Project Information

2-1

2.2 Property Ownership / Management

2-2
2.3 Potential Stormwater Pollutants

2-3
2.4 Water Quality Credits
……………………………………………………………………………. 
2-4
Section 3
Site and Watershed Description

3-1
Section 4
Best Management Practices

4-1


4.1 Source Control and Site Design BMPs

4-1


4.1.1 Source Control BMPs

4-1
4.1.2 Site Design BMPs 

4-6

4.2 Treatment BMPs 

4-7 

4.3 Project Conformance Analysis

4-12

4.3.1 Site Design BMP

4-14

4.3.2 Infiltration BMP

4-16

4.3.4 Biotreatment BMP

4-19

4.3.5 Conformance Summary

4-23

4.3.6 Hydromodification Control BMP

4-24

4.4 Alternative Compliance Plan (if applicable)

4-25
Section 5
Inspection & Maintenance Responsibility Post Construction BMPs

5-1

Section 6
Site Plan and Drainage Plan

6-1


6.1. Site Plan and Drainage Plan

6-1


6.2 Electronic Data Submittal

6-1
Forms
Form 1-1 Project Information

1-1

Form 2.1-1 Description of Proposed Project

2-1  
Form 2.2-1 Property Ownership/Management

2-2 

Form 2.3-1 Pollutants of Concern

2-3
Form 2.4-1 Water Quality Credits

2-4
Form 3-1 Site Location and Hydrologic Features

3-1

Form 3-2 Hydrologic Characteristics

3-2
Form 3-3 Watershed Description

3-3
Form 4.1-1 Non-Structural Source Control BMP

4-2 
Form 4.1-2 Structural Source Control BMP

4-4
Form 4.1-3 Site Design Practices Checklist

4-6
Form 4.2-1 LID BMP Performance Criteria for Design Capture Volume

4-7
Form 4.2-2 Summary of Hydromodification Assessment

4-8
Form 4.2-3 Hydromodification Assessment for Runoff Volume

4-9
Form 4.2-4 Hydromodification Assessment for Time of Concentration

4-10
Form 4.2-5 Hydromodification Assessment for Peak Runoff

4-11
Form 4.3-1 Infiltration BMP Feasibility

4-13
Form 4.3-2 Site Design BMP

4-14
Form 4.3-3 Infiltration LID BMP

4-17
Form 4.3-4 Selection and Evaluation of Biotreatment BMP

4-19
Form 4.3-5 Volume Based Biotreatment – Bioretention and Planter Boxes w/Underdrains

4-20
Form 4.3-6 Volume Based Biotreatment- Constructed Wetlands and Extended Detention

4-21
Form 4.3-7 Flow Based Biotreatment

4-22
Form 4.3-8 Conformance Summary and Alternative Compliance Volume Estimate

4-23
Form 4.3-9 Hydromodification Control BMP

4-24
Form 5-1 BMP Inspection and Maintenance

5-1

Insert Appendix Title if Applicable - Otherwise, please delete text
Insert Appendix Title if Applicable - Otherwise, please delete text
Insert Appendix Title if Applicable - Otherwise, please delete text
Insert Appendix Title if Applicable - Otherwise, please delete text
Insert Appendix Title if Applicable - Otherwise, please delete text
Section I – Introduction 

This WQMP template has been prepared specifically for the Phase II Small MS4 General Permit in the Mojave River Watershed.  This location is within the jurisdiction of the Lahontan Regional Water Quality Control Board (LRWQCB). This document should not be confused with the WQMP template for the Santa Ana Phase I area of San Bernardino County.  

WQMP preparers must refer to the  MS4 Permit for the Mojave Watershed WQMP template and Technical Guidance (TGD) document found at: http://cms.sbcounty.gov/dpw/Land/NPDES.aspx   to find pertinent arid region and Mojave River Watershed specific references and requirements. 

Section 1
Discretionary Permit(s)

	Form 1-1 Project Information

	Project Name   
	     

	Project Owner Contact Name:
	     

	Mailing Address:  
	     
	E-mail Address:  
	     
	Telephone:  
	       

	Permit/Application Number(s):  
	     
	Tract/Parcel Map Number(s):  
	     

	Additional Information/

Comments:
	     

	Description of Project:
	     

	Provide summary of Conceptual WQMP conditions (if previously submitted and approved). Attach complete copy.
	     


Section 2
Project Description

2.1
Project Information
The WQMP shall provide the information listed below. The information provided for Conceptual/ Preliminary WQMP should give sufficient detail to identify the major proposed site design and LID BMPs and other anticipated water quality features that impact site planning. Final Project WQMP must specifically identify all BMP incorporated into the final site design and provide other detailed information as described herein.  
The purpose of this information is to help determine the applicable development category, pollutants of concern, watershed description, and long term maintenance responsibilities for the project, and any applicable water quality credits. This information will be used in conjunction with the information in Section 3, Site Description, to establish the performance criteria and to select the LID BMP or other BMP for the project or other alternative programs that the project will participate in, which are described in Section 4. 

2.1.1 Project Sizing Categorization 

If the Project is greater than 5,000 square feet, and not on the excluded list as found on Section 1.4 of the TGD, the Project is a Regulated Development Project.  

If the Project is creating and/or replacing greater than 2,500 square feet but less than 5,000 square feet of impervious surface area, then it is considered a Site Design Only project.  This criterion is applicable to all development types including detached single family homes that create and/or replace greater than 2,500 square feet of impervious area and are not part of a larger plan of development.  
	Form 2.1-1  Description of Proposed Project

	1 Regulated Development Project Category (Select all that apply):

	 FORMCHECKBOX 
  #1 New development involving the creation of 5,000 ft2 or more of impervious surface collectively over entire site
	 FORMCHECKBOX 
 #2 Significant re-development involving the addition or replacement of 5,000 ft2 or more of impervious surface on an already developed site
	 FORMCHECKBOX 
  #3 Road Project – any road, sidewalk, or bicycle lane project that creates greater than 5,000 square feet of contiguous impervious surface
	 FORMCHECKBOX 
  #4 LUPs – linear underground/overhead projects that has a discrete location with 5,000 sq. ft. or more new constructed impervious surface

	 FORMCHECKBOX 
  Site Design Only   (Project Total Square Feet > 2,500 but < 5,000 sq.ft.)  Will require source control Site Design Measures.  Use the “PCMP” Template. Do not use this WQMP Template.  

	2 Project Area (ft2):  
	     
	3 Number of Dwelling Units:
	     
	4 SIC Code:  
	     

	5 Is Project going to be phased?  Yes  FORMCHECKBOX 
   No  FORMCHECKBOX 
   If yes, ensure that the WQMP evaluates each phase as a distinct DA, requiring LID BMPs to address runoff at time of completion.  


2.2
Property Ownership/Management
Describe the ownership/management of all portions of the project and site.  State whether any infrastructure will transfer to public agencies (City, County, Caltrans, etc.) after project completion. State if a homeowners or property owners association will be formed and be responsible for the long-term maintenance of project stormwater facilities. Describe any lot-level stormwater features that will be the responsibility of individual property owners.
	Form 2.2-1 Property Ownership/Management

	Describe property ownership/management responsible for long-term maintenance of WQMP stormwater facilities:

	     


2.3
Potential Stormwater Pollutants

Best Management Practices (BMP) measures for pollutant generating activities and sources shall be designed consistent with recommendations from the CASQA Stormwater BMP Handbook for New Development and Redevelopment (or an equivalent manual).  Pollutant generating activities must be considered when determining the overall pollutants of concern for the Project as presented in Form 2.3-1.  
Determine and describe expected stormwater pollutants of concern based on land uses and site activities (refer to Table 3-2 in the TGD for WQMP).
	Form 2.3-1 Pollutants of Concern

	Pollutant
	Please check:  
E=Expected, N=Not Expected
	Additional Information and Comments

	Pathogens (Bacterial / Virus)
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Nutrients - Phosphorous
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Nutrients - Nitrogen
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Noxious Aquatic Plants
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Sediment
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Metals
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Oil and Grease
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Trash/Debris
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Pesticides / Herbicides
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Organic Compounds
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Other:      
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Other:      
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     

	Other:      
	E  FORMCHECKBOX 

	N  FORMCHECKBOX 

	     


Section 3
Site and Watershed Description

Describe the project site conditions that will facilitate the selection of BMPs through an analysis of the physical conditions and limitations of the site and its receiving waters. Identify distinct drainage areas (DA) that collect flow from a portion of the site and describe how runoff from each DA (and sub-watershed Drainage Management Areas (DMAs)) is conveyed to the site outlet(s). Refer to Section 3.2 in the TGD for WQMP. The form below is provided as an example. Then complete Forms 3.2 and 3.3 for each DA on the project site. If the project has more than one drainage area for stormwater management, then complete additional versions of these forms for each DA / outlet.  A map presenting the DMAs must be included as an appendix to the WQMP document. 
	Form 3-1  Site Location and Hydrologic Features

	Site coordinates take GPS measurement at  approximate center of site
	Latitude       
	Longitude       
	Thomas Bros Map page       

	1 San Bernardino County climatic region:     FORMCHECKBOX 
  Desert   

	2 Does the site have more than one drainage area (DA):  Yes FORMCHECKBOX 
    No FORMCHECKBOX 
 If no, proceed to Form 3-2. If yes, then use this form to show a conceptual schematic describing DMAs and hydrologic feature connecting DMAs to the site outlet(s). An example is provided below that can be modified for proposed project or a drawing clearly showing DMA and flow routing may be attached

	

	Conveyance
	Briefly describe on-site drainage features to convey runoff that is not retained within a DMA

	DA1 DMA C flows to DA1 DMA A
	Ex. Bioretention overflow to vegetated bioswale with 4’ bottom width, 5:1 side slopes and bed slope of 0.01. Conveys runoff for 1000’ through DMA 1 to existing catch basin on SE corner of property 

	DA1 DMA A to Outlet 1
	     

	DA1 DMA B to Outlet 1
	     

	DA2 to Outlet 2
	     


	Form 3-2 Existing Hydrologic Characteristics for Drainage Area 1 

	For Drainage Area 1’s sub-watershed DMA, provide the following characteristics
	DMA A
	DMA B
	DMA C
	DMA D

	1 DMA drainage area (ft2)
	     
	     
	     
	     

	2 Existing site impervious area (ft2)
	     
	     
	     
	     

	3 Antecedent moisture condition For desert areas, use http://www.sbcounty.gov/dpw/floodcontrol/pdf/20100412_map.pdf
	     
	     
	     
	     

	4 Hydrologic soil group  Refer to  County Hydrology Manual Addendum for Arid Regions –http://www.sbcounty.gov/dpw/floodcontrol/pdf/20100412_addendum.pdf
	     
	     
	     
	     

	5 Longest flowpath length (ft)
	     
	     
	     
	     

	6 Longest flowpath slope (ft/ft)
	     
	     
	     
	     

	7 Current land cover type(s)  Select from Fig C-3 of Hydrology Manual
	     
	     
	     
	     

	8 Pre-developed pervious area condition: Based on the extent of wet season vegetated cover good >75%; Fair 50-75%; Poor  <50% Attach photos of site to support rating
	     
	     
	     
	     


	Form 3-2 Existing Hydrologic Characteristics for Drainage Area 1
(use only as needed for additional DMA w/in DA 1)

	For Drainage Area 1’s sub-watershed DMA, provide the following characteristics
	DMA E
	DMA F
	DMA G
	DMA H

	1 DMA drainage area (ft2)
	     
	     
	     
	     

	2 Existing site impervious area (ft2)
	     
	     
	     
	     

	3 Antecedent moisture condition For desert areas, use http://www.sbcounty.gov/dpw/floodcontrol/pdf/20100412_map.pdf
	     
	     
	     
	     

	4 Hydrologic soil group County Hydrology Manual Addendum for Arid Regions –http://www.sbcounty.gov/dpw/floodcontrol/pdf/20100412_addendum.pdf


	     
	     
	     
	     

	5 Longest flowpath length (ft)
	     
	     
	     
	     

	6 Longest flowpath slope (ft/ft)
	     
	     
	     
	     

	7 Current land cover type(s)  Select from Fig C-3 of Hydrology Manual
	     
	     
	     
	     

	8 Pre-developed pervious area condition: Based on the extent of wet season vegetated cover good >75%; Fair 50-75%; Poor  <50% Attach photos of site to support rating
	     
	     
	     
	     


	Form 3-3 Watershed Description for Drainage Area    

	Receiving waters
Refer to SWRCB site:

http://www.waterboards.ca.gov/water_issues/programs/tmdl/integrated2010.shtml

	     

	Applicable TMDLs

http://www.waterboards.ca.gov/water_issues/programs/tmdl/integrated2010.shtml

	     

	303(d) listed impairments 

http://www.waterboards.ca.gov/water_issues/programs/tmdl/integrated2010.shtml

	     

	Environmentally Sensitive Areas (ESA)

Refer to Watershed Mapping Tool – 

http://sbcounty.permitrack.com/WAP
	     

	Hydromodification Assessment 
	 FORMCHECKBOX 
  Yes Complete Hydromodification Assessment. Include Forms 4.2-2 through Form 4.2-5 and Hydromodification BMP Form 4.3-9 in submittal 
 FORMCHECKBOX 
  No 


Section 4
Best Management Practices (BMP)

4.1
Source Control BMPs and Site Design BMP Measures
The information and data in this section are required for both Regulated Development and Site Design Only Projects. Source Control BMPs and Site Design BMP Measures are the basis of site-specific pollution management. 

4.1.1
Source Control BMPs
Non-structural and structural source control BMP are required to be incorporated into all new development and significant redevelopment projects. Form 4.1-1 and 4.1-2 are used to describe specific source control BMPs used in the WQMP or to explain why a certain BMP is not applicable. Table 7-3 of the TGD for WQMP provides a list of applicable source control BMP for projects with specific types of potential pollutant sources or activities. The source control BMP in this table must be implemented for projects with these specific types of potential pollutant sources or activities.
The preparers of this WQMP have reviewed the source control BMP requirements for new development and significant redevelopment projects. The preparers have also reviewed the specific BMP required for project as specified in Forms 4.1-1 and 4.1-2. All applicable non-structural and structural source control BMP shall be implemented in the project.
The identified list of source control BMPs correspond to the CASQA Stormwater BMP Handbook for New Development and Redevelopment.
	Form 4.1-1 Non-Structural Source Control BMPs

	Identifier
	Name
	Check One
	Describe BMP Implementation OR,

if not applicable, state reason

	
	
	Included
	Not Applicable
	

	N1
	Education of Property Owners, Tenants and Occupants on Stormwater BMPs
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N2
	Activity Restrictions
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N3
	Landscape Management BMPs
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N4
	BMP Maintenance
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N5
	Title 22 CCR Compliance 

(How development will comply)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N6
	Local Water Quality Ordinances
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N7
	Spill Contingency Plan
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N8
	Underground Storage Tank Compliance
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N9
	Hazardous Materials Disclosure Compliance
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     


	Form 4.1-1 Non-Structural Source Control BMPs

	Identifier
	Name
	Check One
	Describe BMP Implementation OR,

if not applicable, state reason

	
	
	Included
	Not Applicable
	

	N10
	Uniform Fire Code Implementation
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N11
	Litter/Debris Control Program
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N12
	Employee Training
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N13
	Housekeeping of Loading Docks
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N14
	Catch Basin Inspection Program
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N15
	Vacuum Sweeping of Private Streets and Parking Lots
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N16
	Other Non-structural Measures for Public Agency Projects
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	N17
	Comply with all other applicable NPDES permits
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     


	Form 4.1-2 Structural Source Control BMPs

	Identifier
	Name
	Check One
	Describe BMP Implementation OR,

If not applicable, state reason

	
	
	Included
	Not Applicable
	

	S1
	Provide storm drain system stencilling and signage (CASQA New Development BMP Handbook SD-13)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S2
	Design and construct outdoor material storage areas to reduce pollution introduction (CASQA New Development BMP Handbook SD-34)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S3
	Design and construct trash and waste storage areas to reduce pollution introduction (CASQA New Development BMP Handbook SD-32)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S4
	Use efficient irrigation systems & landscape design, water conservation, smart controllers, and source control (Statewide Model Landscape Ordinance; CASQA New Development BMP Handbook SD-12)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S5
	Finish grade of landscaped areas at a minimum of 1-2 inches below top of curb, sidewalk, or pavement
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S6
	Protect slopes and channels and provide energy dissipation (CASQA New Development BMP Handbook SD-10)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S7
	Covered dock areas (CASQA New Development BMP Handbook SD-31)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S8
	Covered maintenance bays with spill containment plans (CASQA New Development BMP Handbook SD-31)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S9
	Vehicle wash areas with spill containment plans (CASQA New Development BMP Handbook SD-33)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S10
	Covered outdoor processing areas (CASQA New Development BMP Handbook SD-36)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	Form 4.1-2 Structural Source Control BMPs

	Identifier
	Name
	Check One
	Describe BMP Implementation OR,

If not applicable, state reason

	
	
	Included
	Not Applicable
	

	S11
	Equipment wash areas with spill containment plans (CASQA New Development BMP Handbook SD-33)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S12
	Fueling areas (CASQA New Development BMP Handbook SD-30)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S13
	Hillside landscaping (CASQA New Development BMP Handbook SD-10)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S14
	Wash water control for food preparation areas
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     

	S15
	Community car wash racks (CASQA New Development BMP Handbook SD-33)
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	     


4.1.2
Site Design BMPs
As part of the planning phase of a project, the site design practices associated with new LID requirements in the Phase II Small MS4 Permit must be considered.  Site design BMP measures can result in smaller Design Capture Volume (DCV) to be managed by both LID and hydromodification control BMPs by reducing runoff generation. 
As is stated in the Permit, it is necessary to evaluate site conditions such as soil type(s), existing vegetation and flow paths will influence the overall site design.  

Describe site design and drainage plan including:

· A narrative of site design practices utilized or rationale for not using practices

· A narrative of how site plan incorporates preventive site design practices

· Include an attached Site Plan layout which shows how preventative site design practices are included in WQMP
Refer to Section 5.2 of the TGD for WQMP for more details.

	Form 4.1-3 Site Design Practices Checklist

	Site Design Practices
If yes, explain how preventative site design practice is addressed in project site plan. If no, other LID BMPs must be selected to meet targets

	Minimize impervious areas: Yes  FORMCHECKBOX 
    No  FORMCHECKBOX 

Explanation:      

	Maximize natural infiltration capacity; Including improvement and maintenance of soil: Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Preserve existing drainage patterns and time of concentration: Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Disconnect impervious areas. Including rerouting of rooftop drainage pipes to drain stormwater to storage or infiltration BMPs instead of to storm drain : Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Use of Porous Pavement.:  Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Protect existing vegetation and sensitive areas: Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Re-vegetate disturbed areas. Including planting and preservation of drought tolerant vegetation. : Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Minimize unnecessary compaction in stormwater retention/infiltration basin/trench areas: Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Utilize naturalized/rock-lined drainage swales in place of underground piping or imperviously lined swales: Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Stake off areas that will be used for landscaping to minimize compaction during construction : Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Use of Rain Barrels and Cisterns, Including the use of on-site water collection systems.:   Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      

	Stream Setbacks.  Includes  a specified distance from an adjacent steam: : Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

Explanation:      


It is noted that, in the Phase II Small MS4 Permit, site design elements for green roofs and vegetative swales are required.  Due to the local climatology in the Mojave River Watershed, proactive measures are taken to maximize the amount of drought tolerant vegetation. It is not practical in this region to have green roofs or vegetative swales.   As part of site design the project proponent should utilize locally recommended vegetation types for landscaping.  Typical landscaping recommendations are found in following local references: 
San Bernardino County Special Districts:

Guide to High Desert Landscaping - http://www.specialdistricts.org/Modules/ShowDocument.aspx?documentid=795
Recommended High-Desert Plants - http://www.specialdistricts.org/modules/showdocument.aspx?documentid=553
Mojave Water Agency:
Desert Ranch: http://www.mojavewater.org/files/desertranchgardenprototype.pdf
Summertree: http://www.mojavewater.org/files/Summertree-Native-Plant-Brochure.pdf
Thornless Garden: http://www.mojavewater.org/files/thornlessgardenprototype.pdf
Mediterranean Garden: http://www.mojavewater.org/files/mediterraneangardenprototype.pdf
Lush and Efficient Garden: http://www.mojavewater.org/files/lushandefficientgardenprototype.pdf
Alliance for Water Awareness and Conservation (AWAC) outdoor tips –   http://hdawac.org/save-outdoors.html
4.2
Treatment BMPs
After implementation and design of both Source Control BMPs and Site Design BMP measures, any remaining runoff from impervious DMAs must be directed to one or more on-site, treatment BMPs (LID or biotreatment) designed to infiltrate, evaportranspire, and/or bioretain the amount of runoff specified in Permit Section E.12.e (ii)(c) Numeric Sizing Criteria for Storm Water Retention and Treatment.  
4.2.1 Project Specific Hydrology Characterization
The purpose of this section of the Project WQMP is to establish targets for post-development hydrology based on performance criteria specified in Section E.12.e.ii.c and Section E.12.f of the Phase II Small MS4 Permit. These targets include runoff volume for water quality control (referred to as LID design capture volume), and runoff volume, time of concentration, and peak runoff for protection from hydromodification. 
If the project has more than one outlet for stormwater runoff, then complete additional versions of these forms for each DA / outlet.
It is noted that in the Phase II Small MS4 Permit jurisdictions, the LID BMP Design Capture Volume criteria is based on the 2-year rain event.  The hydromodification performance criterion is based on the 10-year rain event. 
Methods applied in the following forms include:

· For LID BMP Design Capture Volume (DCV), San Bernardino County requires use of the P6 method (Form 4.2-1) For pre- and post-development hydrologic calculation, San Bernardino County requires the use of the Rational Method (San Bernardino County Hydrology Manual Section D). Forms 4.2-2 through Form 4.2-5 calculate hydrologic variables including runoff volume, time of concentration, and peak runoff from the project site pre- and post-development using the Hydrology Manual Rational Method approach. For projects greater than 640 acres (1.0 mi2), the Rational Method and these forms should not be used. For such projects, the Unit Hydrograph Method (San Bernardino County Hydrology Manual Section E) shall be applied for hydrologic calculations for hydromodification performance criteria.

Refer to Section 4 in the TGD for WQMP for detailed guidance and instructions.
	Form 4.2-1  LID BMP Performance Criteria for Design Capture Volume
(DA 1)

	1 Project area DA 1 (ft2):
     
	2 Imperviousness after applying preventative site design practices (Imp%):      
	3 Runoff Coefficient (Rc):  _     
Rc = 0.858(Imp%)^3-0.78(Imp%)^2+0.774(Imp%)+0.04

	4 Determine 1-hour rainfall depth for a 2-year return period P2yr-1hr (in):          http://hdsc.nws.noaa.gov/hdsc/pfds/sa/sca_pfds.html

	5 Compute P6, Mean 6-hr Precipitation (inches):       
P6 = Item 4 *C1, where C1 is a function of site climatic region specified in Form 3-1 Item 1 ( Desert = 1.2371)  

	6 Drawdown Rate 
Use 48 hours as the default condition. Selection and use of the 24 hour drawdown time condition is subject to approval by the local jurisdiction. The necessary BMP footprint is a function of drawdown time. While shorter drawdown times reduce the performance criteria for LID BMP design capture volume, the depth of water that can be stored is also reduced. 
	24-hrs  FORMCHECKBOX 
           
48-hrs  FORMCHECKBOX 


	7 Compute design capture volume, DCV (ft3):        
DCV = 1/12 * [Item 1* Item 3 *Item 5 * C2], where C2 is a function of drawdown rate (24-hr  = 1.582; 48-hr = 1.963) 
Compute separate DCV for each outlet from the project site per schematic drawn in Form 3-1 Item 2


	Form 4.2-2  Summary of Hydromodification Assessment (DA 1)

	Is the change in post- and pre- condition flows captured on-site? :  Yes  FORMCHECKBOX 
    No  FORMCHECKBOX 

If “Yes”, then complete Hydromodification assessment of site hydrology for 10yr storm event using Forms 4.2-3 through 4.2-5 and insert results below (Forms 4.2-3 through 4.2-5 may be replaced by computer software analysis based on the San Bernardino County Hydrology Manual- Addendum 1)
If “No,” then proceed to Section 4.3 BMP Selection and Sizing

	Condition
	Runoff Volume (ft3)
	Time of Concentration (min)
	Peak Runoff (cfs)

	Pre-developed
	1      
Form 4.2-3 Item 12
	2      
Form 4.2-4 Item 13
	3      
Form 4.2-5 Item 10

	Post-developed
	4      
Form 4.2-3 Item 13
	5      
Form 4.2-4 Item 14
	6      
Form 4.2-5 Item 14

	Difference
	7       
Item 4 – Item 1
	8       
Item 2 – Item 5
	9       
Item 6 – Item 3

	Difference 

(as % of pre-developed)
	10      %

Item 7 / Item 1
	11      %

Item 8 / Item 2
	12      %

Item 9 / Item 3


	Form 4.2-3  Hydromodification Assessment for Runoff Volume (DA 1)

	Weighted Curve Number Determination for:

Pre-developed DA
	DMA A
	DMA B
	DMA C
	DMA D
	DMA E
	DMA F
	DMA G
	DMA H

	1a Land Cover type
	     
	     
	     
	     
	     
	     
	     
	     

	2a Hydrologic Soil Group (HSG)
	     
	     
	     
	     
	     
	     
	     
	     

	3a DMA Area, ft2 sum of areas of DMA should equal area of DA
	     
	     
	     
	     
	     
	     
	     
	     

	4a Curve Number (CN) use Items 1 and 2 to select the appropriate CN from Appendix C-2 of the TGD for WQMP
	     
	     
	     
	     
	     
	     
	     
	     

	Weighted Curve Number Determination for:

Post-developed DA
	DMA A
	DMA B
	DMA C
	DMA D
	DMA E
	DMA F
	DMA G
	DMA H

	1b Land Cover type
	     
	     
	     
	     
	     
	     
	     
	     

	2b Hydrologic Soil Group (HSG)
	     
	     
	     
	     
	     
	     
	     
	     

	3b DMA Area, ft2 sum of areas of DMA should equal area of DA
	     
	     
	     
	     
	     
	     
	     
	     

	4b Curve Number (CN) use Items 5 and 6 to select the appropriate CN from Appendix C-2 of the TGD for WQMP
	     
	     
	     
	     
	     
	     
	     
	     

	5 Pre-Developed area-weighted CN:       
	7 Pre-developed soil storage capacity, S (in):       
   S = (1000 / Item 5) - 10
	9 Initial abstraction, Ia (in):      
   Ia = 0.2 * Item 7

	6 Post-Developed area-weighted CN:       
	8 Post-developed soil storage capacity, S (in):      
   S = (1000 / Item 6) - 10
	10 Initial abstraction, Ia (in):      
   Ia = 0.2 * Item 8

	11 Precipitation for 10 yr, 24 hr storm (in):       
   Go to: http://hdsc.nws.noaa.gov/hdsc/pfds/sa/sca_pfds.html

	12 Pre-developed Volume (ft3):       
   Vpre =(1 / 12) * (Item sum of Item 3) * [(Item 11 – Item 9)^2 / ((Item 11 – Item 9 + Item 7)

	13 Post-developed Volume (ft3):       
   Vpre =(1 / 12) * (Item sum of Item 3) * [(Item 11 – Item 10)^2 / ((Item 11 – Item 10 + Item 8)

	14 Volume Reduction needed to meet hydromodification requirement, (ft3):       
   Vhydro = (Item 13 * 0.95) – Item 12


	Form 4.2-4 Hydromodification Assessment for Time of Concentration (DA 1)

	Compute time of concentration for pre and post developed conditions for each DA (For projects using the Hydrology Manual complete the form below)

	Variables
	Pre-developed DA1 

Use additional forms if there are more than 4 DMA
	Post-developed DA1 

Use additional forms if there are more than 4 DMA

	
	DMA A
	DMA B
	DMA C
	DMA D
	DMA A
	DMA B
	DMA C
	DMA D

	1 Length of flowpath (ft)  Use Form 3-2 Item 5 for pre-developed condition
	     
	     
	     
	     
	     
	     
	     
	     

	2 Change in elevation (ft)
	     
	     
	     
	     
	     
	     
	     
	     

	3 Slope (ft/ft), So = Item 2 / Item 1
	     
	     
	     
	     
	     
	     
	     
	     

	4 Land cover
	     
	     
	     
	     
	     
	     
	     
	     

	5 Initial DMA Time of Concentration (min) Appendix C-1 of the TGD for WQMP
	     
	     
	     
	     
	     
	     
	     
	     

	6 Length of conveyance from DMA outlet to project site outlet (ft)  

May be zero if DMA outlet is at project site outlet
	     
	     
	     
	     
	     
	     
	     
	     

	7 Cross-sectional area of channel (ft2)
	     
	     
	     
	     
	     
	     
	     
	     

	8 Wetted perimeter of channel (ft)
	     
	     
	     
	     
	     
	     
	     
	     

	9 Manning’s roughness of channel (n)
	     
	     
	     
	     
	     
	     
	     
	     

	10 Channel flow velocity (ft/sec)  

Vfps = (1.49 / Item 9) * (Item 7/Item 8)^0.67 * (Item 3)^0.5
	     
	     
	     
	     
	     
	     
	     
	     

	11 Travel time to outlet (min) 

Tt = Item 6 / (Item 10 * 60)
	     
	     
	     
	     
	     
	     
	     
	     

	12 Total time of concentration (min) Tc = Item 5 + Item 11
	     
	     
	     
	     
	     
	     
	     
	     

	13 Pre-developed time of concentration (min):            Minimum of Item 12 pre-developed DMA 

	14 Post-developed time of concentration (min):           Minimum of Item 12 post-developed DMA

	15 Additional time of concentration needed to meet hydromodification  requirement (min):         TC-Hydro = (Item 13 * 0.95) – Item 14


	Form 4.2-5 Hydromodification Assessment for Peak Runoff (DA 1)

	Compute peak runoff for pre- and post-developed conditions

	Variables
	Pre-developed DA to Project Outlet (Use additional forms if more than 3 DMA)
	Post-developed DA to Project Outlet (Use additional forms if more than 3 DMA)

	
	DMA A
	DMA B
	DMA C
	DMA A
	DMA B
	DMA C

	1 Rainfall Intensity for storm duration equal to time of concentration  

Ipeak = 10^(LOG Form 4.2-1 Item 4 - 0.7 LOG Form 4.2-4 Item 5 /60)
	     
	     
	     
	     
	     
	     

	2 Drainage Area of each DMA (Acres) 

For DMA with outlet at project site outlet, include upstream DMA (Using example schematic in Form 3-1, DMA A will include drainage from DMA C)
	     
	     
	     
	     
	     
	     

	3 Ratio of pervious area to total area
For DMA with outlet at project site outlet, include upstream DMA (Using example schematic in Form 3-1, DMA A will include drainage from DMA C)
	     
	     
	     
	     
	     
	     

	4 Pervious area infiltration rate (in/hr) 

Use pervious area CN and antecedent moisture condition with Appendix C-3 of the TGD for WQMP
	     
	     
	     
	     
	     
	     

	5 Maximum loss rate (in/hr)   

Fm = Item 3 * Item 4 

Use area-weighted Fm from DMA with outlet at project site outlet, include upstream DMA (Using example schematic in Form 3-1, DMA A will include drainage from DMA C)
	     
	     
	     
	     
	     
	     

	6 Peak Flow from DMA (cfs)  

Qp =Item 2 * 0.9 * (Item 1 - Item 5)
	     
	     
	     
	     
	     
	     

	7 Time of concentration adjustment factor for other DMA to site discharge point 

Form 4.2-4 Item 12 DMA / Other DMA upstream of site discharge point (If ratio is greater than 1.0, then use maximum value of 1.0)
	DMA A
	n/a
	     
	     
	n/a
	     
	     

	
	DMA B
	     
	n/a
	     
	     
	n/a
	     

	
	DMA C
	     
	     
	n/a
	     
	     
	n/a

	8 Pre-developed Qp at Tc for DMA A:         Qp = Item 6DMAA + [Item 6DMAB * (Item 1DMAA - Item 5DMAB)/(Item 1DMAB - Item 5DMAB)* Item 7DMAA/2] + [Item 6DMAC * (Item 1DMAA - Item 5DMAC)/(Item 1DMAC - Item 5DMAC)* Item 7DMAA/3]
	9 Pre-developed Qp at Tc for DMA B:         Qp = Item 6DMAB + [Item 6DMAA * (Item 1DMAB - Item 5DMAA)/(Item 1DMAA - Item 5DMAA)* Item 7DMAB/1] + [Item 6DMAC * (Item 1DMAB - Item 5DMAC)/(Item 1DMAC - Item 5DMAC)* Item 7DMAB/3]
	10 Pre-developed Qp at Tc for DMA C:         Qp = Item 6DMAC + [Item 6DMAA * (Item 1DMAC - Item 5DMAA)/(Item 1DMAA - Item 5DMAA)* Item 7DMAC/1] + [Item 6DMAB * (Item 1DMAC - Item 5DMAB)/(Item 1DMAB - Item 5DMAB)* Item 7DMAC/2]

	10 Peak runoff from pre-developed condition confluence analysis (cfs):         Maximum of Item 8, 9, and 10 (including additional forms as needed)

	11  Post-developed Qp at Tc for DMA A:        Same as Item 8 for post-developed values
	12  Post-developed Qp at Tc for DMA B:       Same as Item 9 for post-developed values
	13 Post-developed Qp at Tc for DMA C:        Same as Item 10 for post-developed values

	14 Peak runoff from post-developed condition confluence analysis (cfs):         Maximum of Item 11, 12, and 13 (including additional forms as needed)

	15 Peak runoff reduction needed to meet Hydromodification Requirement (cfs):          Qp-hydro = (Item 14 * 0.95) – Item 10


4.3
BMP Selection and Sizing
Complete the following forms for each project site DA to document that the proposed treatment (LID/Bioretention) BMPs conform to the project DCV developed to meet performance criteria specified in the Phase II Small MS4 Permit (WQMP Template Section 4.2). For the LID DCV, the forms are ordered according to hierarchy of BMP selection as required by the Phase II Small MS4 Permit (see Section 5.3 in the TGD for WQMP). The forms compute the following for on-site LID BMP: 
· Site Design Measures (Form 4.3-2)

· Retention and Infiltration BMPs (Form 4.3-3) or
· Biotreatment BMPs (Form 4.3-4). 

At the end of each form, additional fields facilitate the determination of the extent of mitigation provided by the specific BMP category, allowing for use of the next category of BMP in the hierarchy, if necessary.

The first step in the analysis, using Section 5.3.2 of the TGD for WQMP, is to complete Forms 4.3-1 and 4.3-3) to determine if retention and infiltration BMPs are infeasible for the project. For each feasibility criterion in Form 4.3-1, if the answer is “Yes,” provide all study findings that includes relevant calculations, maps, data sources, etc. used to make the determination of infeasibility.
Next, complete Form 4.3-2 to determine the feasibility of applicable Site Design BMPs, and, if their implementation is feasible, the extent of mitigation of the DCV.

If no site constraints exist that would limit the type of BMP to be implemented in a DA, evaluate the use of combinations of LID BMPs, including all applicable Site Design BMPs to maximize on-site retention of the DCV. If no combination of BMP can mitigate the entire DCV, implement the single BMP type, or combination of BMP types, that maximizes on-site retention of the DCV within the minimum effective area. 

If the combination of site design, retention and/or infiltration BMPs is unable to mitigate the entire DCV, then the remainder of the volume-based performance criteria that cannot be achieved with site design, retention and/or infiltration BMPs must be managed through biotreatment BMPs. If biotreatment BMPs are used, then they must be sized to provide equivalent effectiveness based on Template Section 4.3.4. 

4.3.1 Exceptions to Requirements for Bioretention Facilities

Contingent on a demonstration that use of bioretention or a facility of equivalent effectiveness is infeasible, other types of biotreatment or media filters (such as tree-box-type biofilters or in-vault media filters) may be used for the following categories of Regulated Projects: 

1) Projects creating or replacing an acre or less of impervious area, and located in a designated pedestrian-oriented commercial district (i.e., smart growth projects), and having at least 85% of the entire project site covered by permanent structures; 

2) Facilities receiving runoff solely from existing (pre-project) impervious areas; and 

3) Historic sites, structures or landscapes that cannot alter their original configuration in order to maintain their historic integrity. 

	Form 4.3-1 Infiltration BMP Feasibility (DA 1)

	Feasibility Criterion – Complete evaluation for each DA on the Project Site

	1 Would infiltration BMP pose significant risk for groundwater related concerns?                                                           Yes  FORMCHECKBOX 
   No  FORMCHECKBOX 

Refer to Section 5.3.2.1 of the TGD for WQMP 

	If Yes, Provide basis: (attach)

	2 Would installation of infiltration BMP significantly increase the risk of geotechnical hazards?                                   Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

(Yes, if the answer to any of the following questions is yes, as established by a geotechnical expert): 

· The location is less than 50 feet away from slopes steeper than 15 percent

· The location is less than ten feet from building foundations or an alternative setback.
· A study certified by a geotechnical professional or an available watershed study determines that stormwater infiltration would result in significantly increased risks of geotechnical hazards.

	If Yes, Provide basis: (attach)

	3 Would infiltration of runoff on a Project site violate downstream water rights?                                                             Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 


	If Yes, Provide basis: (attach)

	4 Is proposed infiltration facility located on hydrologic soil group (HSG) D soils or does the site geotechnical investigation indicate presence of soil characteristics, which support categorization as D soils?                                                                            Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 


	If Yes, Provide basis: (attach)

	5 Is the design infiltration rate, after accounting for safety factor of 2.0, below proposed facility less than 0.3 in/hr (accounting for soil amendments)?                                                                                                                                                                            Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 


	If Yes, Provide basis: (attach)

	6 Would on-site infiltration or reduction of runoff over pre-developed conditions be partially or fully inconsistent with watershed management strategies as defined in the WAP, or impair beneficial uses?                                                                           Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

See Section 3.5 of the TGD for WQMP and WAP

	If Yes, Provide basis: (attach)

	7 Any answer from Item 1 through Item 3 is “Yes”:                                                                                                                     Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 
  
If yes, infiltration of any volume is not feasible onsite. Proceed to Form 4.3-4, Selection and Evaluation of Biotreatment BMP.          If no, then proceed to Item 8 below.

	8 Any answer from Item 4 through Item 6 is “Yes”:                                                                                                                      Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 
  
If yes, infiltration is permissible but is not required to be considered. Proceed to Form 4.3-2, Site Design BMP. 
If no, then proceed to Item 9, below.

	9 All answers to Item 1 through Item 6 are “No”:  
Infiltration of the full DCV is potentially feasible, LID infiltration BMP must be designed to infiltrate the full DCV to the MEP.
Proceed to Form 4.3-2, Site Design BMPs.


4.3.2
Site Design  BMP

Section E.12.e. of the Small Phase II MS4 Permit emphasizes the use of LID preventative measures; and the use of Site Design Measures reduces the portion of the DCV that must be addressed in downstream BMPs. Therefore, all applicable Site Design Measures shall be provided except where they are mutually exclusive with each other, or with other BMPs. Mutual exclusivity may result from overlapping BMP footprints such that either would be potentially feasible by itself, but both could not be implemented. Please note that while there are no numeric standards regarding the use of Site Design BMPs. If a project cannot feasibly meet BMP sizing requirements or cannot fully address hydromodification, feasibility of all applicable Site Design BMPs must be part of demonstrating that the BMP system has been designed to retain the maximum feasible portion of the DCV. Complete Form 4.3-2 to identify and calculate estimated retention volume from implementing site design BMP. Refer to Section 5.4 in the TGD for more detailed guidance.
	Form 4.3-2  Site Design BMPs (DA 1)

	1 Implementation of Impervious Area Dispersion BMP (i.e. routing runoff from impervious to pervious areas), excluding impervious areas planned for routing to on-lot infiltration BMP:  Yes  FORMCHECKBOX 
   No  FORMCHECKBOX 
   If yes, complete Items 2-5; If no, proceed to Item 6
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type        (Use additional forms for more BMPs)

	2 Total impervious area draining to pervious area (ft2)
	     
	     
	     

	3 Ratio of pervious area receiving runoff to impervious area
	     
	     
	     

	4 Retention volume achieved from impervious area dispersion (ft3)   V = Item2 * Item 3 * (0.5/12), assuming retention of 0.5 inches of runoff
	     
	     
	     

	5 Sum of retention volume achieved from impervious area dispersion (ft3):             Vretention =Sum of Item 4 for all BMPs

	6 Implementation of Localized On-lot Infiltration BMPs (e.g. on-lot rain gardens):  Yes  FORMCHECKBOX 
   No  FORMCHECKBOX 
   If yes, complete Items 7-13 for aggregate of all on-lot infiltration BMP in each DA; If no, proceed to Item 14
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type        (Use additional forms for more BMPs)

	7 Ponding surface area (ft2)
	     
	     
	     

	8 Ponding depth (ft) (min. 0.5 ft.)
	     
	     
	     

	9 Surface area of amended soil/gravel (ft2)
	     
	     
	     

	10 Average depth of amended soil/gravel (ft) (min. 1 ft.)
	     
	     
	     

	11 Average porosity of amended soil/gravel
	     
	     
	     

	12 Retention volume achieved from on-lot infiltration (ft3)

Vretention = (Item 7 *Item 8) + (Item 9 * Item 10 * Item 11)
	     
	     
	     

	13 Runoff volume retention from on-lot infiltration (ft3):             Vretention =Sum of Item 12 for all BMPs

	

	Form 4.3-2 cont. Site Design BMPs (DA 1)

	

	14 Implementation of Street Trees:   Yes   FORMCHECKBOX 
     No   FORMCHECKBOX 
  

If yes, complete Items 14-18.  If no, proceed to Item 19 
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type        (Use additional forms for more BMPs)

	15 Number of Street Trees
	     
	     
	     

	16 Average canopy cover over impervious area (ft2)
	     
	     
	     

	17 Runoff volume retention from street trees (ft3) 

Vretention = Item 15 * Item 16 * (0.05/12) assume runoff retention of 0.05 inches
	     
	     
	     

	18 Runoff volume retention from street tree BMPs (ft3):              Vretention = Sum of Item 17 for all BMPs

	19 Total Retention Volume from Site Design BMPs:         Sum of Items 5, 13 and  18 


4.3.3
 Infiltration BMPs

Use Form 4.3-3 to compute on-site retention of runoff from proposed retention and infiltration BMPs. Volume retention estimates are sensitive to the percolation rate used, which determines the amount of runoff that can be infiltrated within the specified drawdown time. The infiltration safety factor reduces field measured percolation to account for potential inaccuracy associated with field measurements, declining BMP performance over time, and compaction during construction. Appendix C of the TGD for WQMP provides guidance on estimating an appropriate safety factor to use in Form 4.3-3. 
If site constraints limit the use of BMPs to a single type and implementation of retention and infiltration BMPs mitigate no more than 40% of the DCV, then they are considered infeasible and the Project Proponent may evaluate the effectiveness of BMPs lower in the LID hierarchy of use (Section 5.5 of the TGD for WQMP)
If implementation of infiltrations BMPs is feasible as determined using Form 4.3-1, then LID infiltration BMPs shall be implemented to the MEP (section 4.1 of the TGD for WQMP). 

4.3.3.1 Allowed Variations for Special Site Conditions 
The bioretention system design parameters of this Section may be adjusted for the following special site conditions: 

1) Facilities located within 10 feet of structures or other potential geotechnical hazards established by the geotechnical expert for the project may incorporate an impervious cutoff wall between the bioretention facility and the structure or other geotechnical hazard. 

2) Facilities with documented high concentrations of pollutants in underlying soil or groundwater, facilities located where infiltration could contribute to a geotechnical hazard, and facilities located on elevated plazas or other structures may incorporate an impervious liner and may locate the underdrain discharge at the bottom of the subsurface drainage/storage layer (this configuration is commonly known as a “flow-through planter”). 

3) Facilities located in areas of high groundwater, highly infiltrative soils or where connection of underdrain to a surface drain or to a subsurface storm drain are infeasible, may omit the underdrain. 

4) Facilities serving high-risk areas such as fueling stations, truck stops, auto repairs, and heavy industrial sites may be required to provide adequate pretreatment to address pollutants of concern unless these high-risk areas are isolated from storm water runoff or bioretention areas with no chance of spill migration. 

.

	Form 4.3-3  Infiltration LID BMP - including underground BMPs (DA 1)

	1 Remaining LID DCV not met by site design BMP (ft3):          Vunmet = Form 4.2-1 Item 7 - Form 4.3-2 Item19

	BMP Type  Use columns to the right to compute runoff volume retention from proposed infiltration BMP (select BMP from Table 5-4 in TGD for WQMP) -  Use additional forms for more BMPs
	DA      DMA    
BMP Type       
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type        
(Use additional forms for more BMPs)

	2 Infiltration rate of underlying soils (in/hr) See Section 5.4.2 and Appendix C of the TGD for WQMP for minimum requirements for assessment methods
	     
	     
	     

	3 Infiltration safety factor  See TGD Section 5.4.2 and Appendix D
	     
	     
	     

	4 Design percolation rate (in/hr)  Pdesign = Item 2 / Item 3
	     
	     
	     

	5 Ponded water drawdown time (hr) Copy Item 6 in Form 4.2-1
	     
	     
	     

	6 Maximum ponding depth (ft)  BMP specific, see Table 5-4 of the TGD for WQMP for BMP design details
	     
	     
	     

	7 Ponding Depth (ft)  dBMP = Minimum of (1/12*Item 4*Item 5) or Item 6
	     
	     
	     

	8 Infiltrating surface area, SABMP (ft2) the lesser of the area needed for infiltration of full DCV or minimum space requirements from Table 5.7 of the TGD for WQMP
	     
	     
	     

	9 Amended soil depth, dmedia (ft)  Only included in certain BMP types, see  Table 5-4 in the TGD for WQMP for reference to BMP design details
	     
	     
	     

	10 Amended soil porosity
	     
	     
	     

	11 Gravel depth, dmedia (ft) Only included in certain BMP types,  see Table 5-4 of the TGD for WQMP for BMP design details
	     
	     
	     

	12 Gravel porosity
	     
	     
	     

	13 Duration of storm as basin is filling (hrs)  Typical ~ 3hrs
	     
	     
	     

	14 Above Ground Retention Volume (ft3)  Vretention = Item 8 * [Item7 + (Item 9 * Item 10) + (Item 11 * Item 12) + (Item 13 * (Item 4 / 12))]
	     
	     
	     

	15 Underground Retention Volume (ft3)  Volume determined using manufacturer’s specifications and calculations
	     
	     
	     

	16 Total Retention Volume from LID Infiltration BMPs:          (Sum of Items 14 and 15 for all infiltration BMP included in plan)

	17  Fraction of DCV achieved with infiltration BMP:      %   Retention% = Item 16 / Form 4.2-1 Item 7

	18 Is full LID DCV retained onsite with combination of hydrologic source control and LID retention/infiltration BMPs? Yes  FORMCHECKBOX 
  No  FORMCHECKBOX 
 

 If yes, demonstrate conformance using Form 4.3-10; If no, then reduce Item 3, Factor of Safety to 2.0 and increase Item 8, Infiltrating Surface Area, such that the portion of the site area used for retention and infiltration BMPs equals or exceeds the minimum effective area thresholds (Table 5-7 of the TGD for WQMP) for the applicable category of development and repeat all above calculations.


4.3.4
Biotreatment BMP

Biotreatment BMPs may be considered if the full LID DCV cannot be met by maximizing retention and infiltration. A key consideration when using biotreatment BMP is the effectiveness of the proposed BMP in addressing the pollutants of concern for the project (see Table 5-5 of the TGD for WQMP).
Use Form 4.3-4 to summarize the potential for volume based and/or flow based biotreatment options to biotreat the remaining unmet LID DCV.  Biotreatment computations are included as follows:
· Use Form 4.3-5 to compute biotreatment in small volume based biotreatment BMP (e.g. bioretention w/underdrains); 

· Use Form 4.3-6 to compute biotreatment in large volume based biotreatment BMP (e.g. constructed wetlands);

· Use Form 4.3-7 to compute sizing criteria for flow-based biotreatment BMP (e.g. bioswales)

	Form 4.3-4 Selection and Evaluation of Biotreatment BMP (DA 1)

	1 Remaining LID DCV not met by site design , or infiltration, BMP for potential biotreatment (ft3):           Form 4.2-1 Item 7 - Form 4.3-2 Item 19 – Form 4.3-3 Item 16 
	List pollutants of concern   Copy from Form 2.3-1.

     


	2 Biotreatment BMP Selected  (Select biotreatment BMP(s) necessary to ensure all pollutants of concern are addressed through Unit Operations and Processes, described in Table 5-5 of the TGD for WQMP)
	Volume-based biotreatment 

Use Forms 4.3-5 and 4.3-6 to compute treated volume
	Flow-based biotreatment  

Use Form 4.3-7 to compute treated flow 

	
	 FORMCHECKBOX 
 Bioretention with underdrain

 FORMCHECKBOX 
 Planter box with underdrain

 FORMCHECKBOX 
 Constructed wetlands

 FORMCHECKBOX 
Wet extended detention

 FORMCHECKBOX 
 Dry extended detention
	 FORMCHECKBOX 
 Vegetated swale

 FORMCHECKBOX 
Vegetated filter strip

 FORMCHECKBOX 
 Proprietary biotreatment

	3 Volume biotreated in volume based biotreatment BMP (ft3):        Form 4.3-5 Item 15 + Form 4.3-6 Item 13
	4 Compute remaining LID DCV with implementation of volume based biotreatment BMP (ft3):          Item 1 – Item 3
	5 Remaining fraction of LID DCV for sizing flow based biotreatment BMP:      %  Item 4  / Item 1

	6 Flow-based biotreatment BMP capacity provided (cfs):         Use Figure 5-2 of the TGD for WQMP to determine flow capacity required to provide biotreatment of remaining percentage of unmet LID DCV (Item 5), for the project’s precipitation zone (Form 3-1 Item 1)

	7 Metrics for MEP determination: 

· Provided a WQMP with the portion of site area used for suite of LID BMP equal to minimum thresholds in Table 5-7 of the TGD for WQMP for the proposed category of development:   FORMCHECKBOX 
  If maximized on-site retention BMPs is feasible for partial capture, then LID BMP implementation must be optimized to retain and infiltrate the maximum portion of the DCV possible within the prescribed minimum effective area. The remaining portion of the DCV shall then be mitigated using biotreatment BMP. 


	Form 4.3-5 Volume Based Biotreatment (DA 1) – 
Bioretention and Planter Boxes with Underdrains

	Biotreatment BMP Type 
(Bioretention w/underdrain, planter box w/underdrain, other comparable BMP)
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type        
(Use additional forms for more BMPs)

	1 Pollutants addressed with BMP    List all pollutant of concern that will be effectively reduced through specific Unit Operations and Processes described in Table 5-5 of the TGD for WQMP 
	     
	     
	     

	2 Amended soil infiltration rate Typical ~ 5.0
	     
	     
	     

	3 Amended soil infiltration safety factor Typical ~ 2.0
	     
	     
	     

	4 Amended soil design percolation rate (in/hr) Pdesign = Item 2 / Item 3
	     
	     
	     

	5 Ponded water drawdown time (hr) Copy Item 6 from Form 4.2-1
	     
	     
	     

	6 Maximum ponding depth (ft)  see Table 5-6 of the TGD for WQMP for reference to BMP design details
	     
	     
	     

	7 Ponding Depth (ft)  dBMP = Minimum of (1/12 * Item 4 * Item 5) or Item 6
	     
	     
	     

	8 Amended soil surface area (ft2)
	     
	     
	     

	9 Amended soil depth (ft)  see Table 5-6 of the TGD for WQMP for reference to BMP design details
	     
	     
	     

	10 Amended soil porosity, n
	     
	     
	     

	11 Gravel depth (ft)  see Table 5-6 of the TGD for WQMP for reference to BMP design details
	     
	     
	     

	12 Gravel porosity, n
	     
	     
	     

	13  Duration of storm as basin is filling (hrs)  Typical ~ 3hrs
	     
	     
	     

	14 Biotreated Volume (ft3)     Vbiotreated = Item 8 * [(Item 7/2) + (Item 9 * Item 10) +(Item 11 * Item 12) + (Item 13 * (Item 4 / 12))]
	     
	     
	     

	15 Total biotreated  volume from bioretention and/or planter box  with underdrains BMP:         
Sum of Item 14 for all volume-based BMPs included in this form


	Form 4.3-6 Volume Based Biotreatment (DA 1) – 

Constructed Wetlands and Extended Detention

	Biotreatment BMP Type 
Constructed wetlands, extended wet detention, extended dry detention, or other comparable proprietary BMP. If BMP includes multiple modules 

(E.g. forebay and main basin), provide separate estimates for storage and pollutants treated in each module.
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type      
(Use additional forms

 for more BMPs)

	
	Forebay
	Basin
	Forebay
	Basin

	1 Pollutants addressed with BMP forebay and basin

List all pollutant of concern that will be effectively reduced through specific Unit Operations and Processes described in Table 5-5 of the TGD for WQMP
	     
	     
	     
	     

	2 Bottom width (ft)
	     
	     
	     
	     

	3 Bottom length (ft)
	     
	     
	     
	     

	4 Bottom area (ft2) Abottom = Item 2 * Item 3
	     
	     
	     
	     

	5 Side slope (ft/ft)  
	     
	     
	     
	     

	6 Depth of storage (ft) 
	     
	     
	     
	     

	7 Water surface area (ft2) 

Asurface =(Item 2 + (2 * Item 5 * Item 6)) * (Item 3 + (2 * Item 5 * Item 6))
	     
	     
	     
	     

	8 Storage volume (ft3) For BMP with a forebay, ensure fraction of total storage is within ranges specified in BMP specific fact sheets, see Table 5-6 of the TGD for WQMP for reference to BMP design details
V =Item 6 / 3 * [Item 4 + Item 7 + (Item 4 * Item 7)^0.5] 
	     
	     
	     
	     

	9 Drawdown Time (hrs)  Copy Item 6 from Form 2.1
	     
	     

	10 Outflow rate (cfs) QBMP = (Item 8forebay + Item 8basin) / (Item 9 * 3600)
	     
	     

	11 Duration of design storm event (hrs)
	     
	     

	12 Biotreated Volume (ft3) 

Vbiotreated = (Item 8forebay + Item 8basin) +( Item 10 * Item 11 * 3600)
	     
	     

	13 Total biotreated volume from constructed wetlands, extended dry detention, or extended wet detention :         
 (Sum of Item 12 for all BMP included in plan)


	Form 4.3-7 Flow Based Biotreatment (DA 1)

	Biotreatment BMP Type
Vegetated swale, vegetated filter strip, or other comparable proprietary BMP
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type      
	DA      DMA    
BMP Type        
(Use additional forms for more BMPs)

	1 Pollutants addressed with BMP

List all pollutant of concern that will be effectively reduced through specific Unit Operations and Processes described in TGD Table 5-5
	     
	     
	     

	2 Flow depth for water quality treatment (ft) 

BMP specific, see Table 5-6 of the TGD for WQMP for reference to BMP design details
	     
	     
	     

	3 Bed slope (ft/ft) 

BMP specific, see Table 5-6 of the TGD for WQMP for reference to BMP design details
	     
	     
	     

	4 Manning's roughness coefficient
	     
	     
	     

	5 Bottom width (ft) 

bw = (Form 4.3-5 Item 6 * Item 4) / (1.49 * Item 2^1.67 * Item 3^0.5)
	     
	     
	     

	6 Side Slope (ft/ft) 

BMP specific, see Table 5-6 of the TGD for WQMP for reference to BMP design details
	     
	     
	     

	7 Cross sectional area (ft2) 

A = (Item 5 * Item 2) + (Item 6 * Item 2^2)
	     
	     
	     

	8 Water quality flow velocity (ft/sec)

V =  Form 4.3-5 Item 6 / Item 7
	     
	     
	     

	9 Hydraulic residence time (min) 

Pollutant specific, see Table 5-6 of the TGD for WQMP for reference to BMP design details
	     
	     
	     

	10 Length of flow based BMP (ft)

L = Item 8 * Item 9 * 60
	     
	     
	     

	11 Water surface area at water quality flow depth (ft2) 

SAtop = (Item 5 + (2 * Item 2 * Item 6)) * Item 10
	     
	     
	     


4.3.5
Conformance Summary

Complete Form 4.3-8 to demonstrate how on-site LID DCV is met with proposed site design, infiltration, and/or biotreatment BMP. The bottom line of the form is used to describe the basis for infeasibility determination for on-site LID BMP to achieve full LID DCV, and provides methods for computing remaining volume to be addressed in an alternative compliance plan. If the project has more than one outlet, then complete additional versions of this form for each outlet.  
	Form 4.3-8 Conformance Summary and Alternative 
Compliance Volume Estimate (DA 1)

	1 Total LID DCV for the Project DA-1 (ft3):         Copy Item 7 in Form 4.2-1

	2 On-site retention with site design BMP (ft3):         Copy Item18 in Form 4.3-2

	3 On-site retention with LID infiltration BMP (ft3):          Copy Item 16 in Form 4.3-3

	4 On-site biotreatment with volume based biotreatment BMP (ft3):           Copy Item 3 in Form 4.3-4

	5 Flow capacity provided by flow based biotreatment BMP (cfs):          Copy Item 6 in Form 4.3-4

	6 LID BMP performance criteria are achieved if answer to any of the following is “Yes”:

· Full retention of LID DCV with site design  or infiltration BMP:   Yes  FORMCHECKBOX 
  No  FORMCHECKBOX 
 
If yes, sum of Items 2, 3, and 4 is greater than Item 1
· Combination of on-site retention BMPs for a portion of the LID DCV and volume-based biotreatment BMP that address all pollutants of concern for the remaining LID DCV:  Yes  FORMCHECKBOX 
 No  FORMCHECKBOX 

If yes, a) sum of Items 2, 3, 4, and 5 is greater than Item 1, and Items 2, 3 and 4 are maximized; or b) Item 6 is greater than Form 4.3‑‑5 Item 6 and Items 2, 3 and 4 are maximized
· On-site retention and infiltration is determined to be infeasible; therefore biotreatment BMP provides biotreatment for all pollutants of concern for full LID DCV:  Yes  FORMCHECKBOX 
  No  FORMCHECKBOX 
 
If yes, Form 4.3-1 Items 7 and 8 were both checked yes

	7 If the LID DCV is not achieved by any of these means, then the project may be allowed to develop an alternative compliance plan. Check box that describes the scenario which caused the need for alternative compliance:
· Combination of Site Design, retention and infiltration, , and biotreatment BMPs provide less than full LID DCV capture:    FORMCHECKBOX 

Checked yes if Form 4.3-4 Item 7is checked yes, Form 4.3-4 Item 6 is zero, and sum of Items 2, 3, 4, and 5 is less than Item 1. If so, apply water quality credits and calculate volume for alternative compliance,  Valt = (Item 1 – Item 2 – Item 3 – Item 4 – Item 5) * (100 - Form 2.4-1 Item 2)%
· Facilities, or a combination of facilities, of a different design than in Section E.12.e.(ii)(f) may be permitted if all of the following Phase II Small MS4 General Permit 2013-0001-DWQ 55 February 5, 2013 measures of equivalent effectiveness are demonstrated:

1) Equal or greater amount of runoff infiltrated or evapotranspired;     FORMCHECKBOX 

2) Equal or lower pollutant concentrations in runoff that is discharged after biotreatment;     FORMCHECKBOX 

3) Equal or greater protection against shock loadings and spills;     FORMCHECKBOX 

4) Equal or greater accessibility and ease of inspection and maintenance.     FORMCHECKBOX 




4.3.6
Hydromodification Control BMP
Use Form 4.3-9 to compute the remaining runoff volume retention, after Site Design BMPs are implemented, needed to address hydromodification, and the increase in time of concentration and decrease in peak runoff necessary to meet targets for protection of waterbodies with a potential hydromodification. Describe the proposed hydromodification treatment control BMP.   Section 5.6 of the TGD for WQMP provides additional details on selection and evaluation of hydromodification control BMP.
	Form 4.3-9 Hydromodification Control BMPs (DA 1)

	1 Volume reduction needed for hydromodification performance criteria (ft3):           

(Form 4.2-2 Item 4 * 0.95) – Form 4.2-2 Item 1
	2 On-site retention with site design and infiltration, BMP (ft3):         Sum of Form 4.3-8 Items 2, 3, and 4.  Evaluate option to increase implementation of on-site retention in Forms 4.3-2, 4.3-3, and 4.3-4 in excess of LID DCV toward achieving hydromodification  volume reduction

	3 Remaining volume for hydromodification volume capture (ft3):        Item 1 – Item 2
	4 Volume capture provided by incorporating additional on-site BMPs (ft3):         

	5 Is Form 4.2-2 Item 11 less than or equal to 5%:   Yes  FORMCHECKBOX 
  No  FORMCHECKBOX 

If yes, hydromodification performance criteria is achieved. If no, select one or more mitigation options below:
· Demonstrate increase in time of concentration achieved by proposed LID site design, LID BMP, and additional on-site BMP   FORMCHECKBOX 

· Increase time of concentration by preserving pre-developed flow path and/or increase travel time by reducing slope and increasing cross-sectional area and roughness for proposed on-site conveyance facilities  FORMCHECKBOX 



	6 Form 4.2-2 Item 12 less than or equal to 5%:   Yes  FORMCHECKBOX 
  No  FORMCHECKBOX 

If yes, hydromodification performance criteria is achieved. If no, select one or more mitigation options below:
· Demonstrate reduction in peak runoff achieved by proposed LID site design, LID BMPs, and additional on-site retention BMPs   FORMCHECKBOX 



4.4
Alternative Compliance Plan (if applicable)
Describe an alternative compliance plan (if applicable) for projects not fully able to infiltrate, or biotreat the DCV via on-site LID practices. A project proponent must develop an alternative compliance plan to address the remainder of the LID DCV. Depending on project type some projects may qualify for water quality credits that can be applied to reduce the DCV that must be treated prior to development of an alternative compliance plan (see Form 2.4-1, Water Quality Credits). Form 4.3-9 Item 8 includes instructions on how to apply water quality credits when computing the DCV that must be met through alternative compliance. 
Alternative Designs — Facilities, or a combination of facilities, of a different design than in Permit Section E.12.e.(ii)(f) may be permitted if all of the following measures of equivalent effectiveness are demonstrated: 

1) Equal or greater amount of runoff infiltrated or evapotranspired; 

2) Equal or lower pollutant concentrations in runoff that is discharged after biotreatment; 

3) Equal or greater protection against shock loadings and spills; 

4) Equal or greater accessibility and ease of inspection and maintenance. 

The Project Proponent will need to obtain written approval for an alternative design from the Lahontan Regional Water Board Executive Officer (see Section 6 of the TGD for WQMP).
Section 5
Inspection and Maintenance Responsibility 
for Post Construction BMP

All BMPs included as part of the project WQMP are required to be maintained through regular scheduled inspection and maintenance (refer to Section 8, Post Construction BMP Requirements, in the TGD for WQMP). Fully complete Form 5-1 summarizing all BMP included in the WQMP. Attach additional forms as needed. The WQMP shall also include a detailed Operation and Maintenance Plan for all BMP and a Maintenance Agreement. The Maintenance Agreement must also be attached to the WQMP.  
	Form 5-1 BMP Inspection and Maintenance
(use additional forms as necessary)

	BMP
	Reponsible Party(s)
	Inspection/ Maintenance

Activities Required
	Minimum Frequency of Activities

	     
	     
	     
	     

	     
	     
	     
	     

	     
	     
	     
	     

	     
	     
	     
	     

	     
	     
	     
	     

	     
	     
	     
	     

	     
	     
	     
	     

	     
	     
	     
	     


Section 6
WQMP Attachments
6.1.
Site Plan and Drainage Plan 

Include a site plan and drainage plan sheet set containing the following minimum information:

· Project location

· Site boundary

· Land uses and land covers, as applicable

· Suitability/feasibility constraints

· Structural Source Control BMP locations

· Site Design Hydrologic Source Control BMP locations

· LID BMP details

· Drainage delineations and flow information

· Drainage connections

6.2
Electronic Data Submittal
Minimum requirements include submittal of PDF exhibits in addition to hard copies. Format must not require specialized software to open. If the local jurisdiction requires specialized electronic document formats (as described in their Local Implementation Plan), this section will describe the contents (e.g., layering, nomenclature, geo-referencing, etc.) of these documents so that they may be interpreted efficiently and accurately.
6.3
Post Construction 

Attach all O&M Plans and Maintenance Agreements for BMP to the WQMP.
6.4
Other Supporting Documentation
· BMP Educational Materials

· Activity Restriction – C,C&R’s & Lease Agreements
Please note that the selected BMPs may also be used as dual purpose for on-site, hydromodification mitigation and management.





Note that at time of Project construction completion, the Maintenance Agreement must be completed, signed, notarized and submitted to the County Stormwater Department 








Contents

COMPANY
Page 37
Date
File Name

Owner’s Certification


